## HW-Plant
SBS Standard I/O Points — HW-Plant ¦ Updated: 2026-03-31 ¦ IO Schedule Rev
Terminal | Point Name | Description | Type | Units | Min | Max | Notes
HW Plant Core
IN1 | HWS-T | Hot Water Supply Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN2 | HWR-T | Hot Water Return Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN3 | OAT | Outside Air Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN4 | OAH | Outside Air Humidity | AI | % |  |  | Range: 0 ->100% (0-5V)
Cascade Boiler Control (2)
IN5 | BLR{N}-ALARM | Boiler 1 Alarm Contact | BI |  |  |  | Range: Normal/Alarm
IN6 | BLR{N}-ALARM | Boiler 2 Alarm Contact | BI |  |  |  | Range: Normal/Alarm
IN9 | BLR{N}-HWST | Boiler 1 HW Supply Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN10 | BLR{N}-HWRT | Boiler 1 HW Return Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN11 | BLR{N}-HWST | Boiler 2 HW Supply Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN12 | BLR{N}-HWRT | Boiler 2 HW Return Temperature | AI | °F |  |  | Range: 10K -40 ->250
OUT1 | BLRS-ENABLE | Boilers Enable Contact | BO |  |  |  | Range: Stop/Start
OUT2 | BLRS-SPT-AO | Boiler Setpoint Analog Output (0-10V) | AO |  |  |  | Range: 0.0 ->100%
Full Boiler Control (2)
IN5 | BLR{N}-ALARM | Boiler 1 Alarm Contact | BI |  |  |  | Range: Normal/Alarm
IN9 | BLR{N}-HWST | Boiler 1 HW Supply Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN10 | BLR{N}-HWRT | Boiler 1 HW Return Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN6 | BLR{N}-ALARM | Boiler 2 Alarm Contact | BI |  |  |  | Range: Normal/Alarm
IN11 | BLR{N}-HWST | Boiler 2 HW Supply Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN12 | BLR{N}-HWRT | Boiler 2 HW Return Temperature | AI | °F |  |  | Range: 10K -40 ->250
OUT1 | BLR{N}-S/S | Boiler 1 Start/Stop | BO |  |  |  | Range: Stop/Start
OUT5 | BLR{N}-MOD | Boiler 1 Fire Rate (0-10V) | AO |  |  |  | Range: 0.0 ->100%
OUT2 | BLR{N}-S/S | Boiler 2 Start/Stop | BO |  |  |  | Range: Stop/Start
OUT6 | BLR{N}-MOD | Boiler 2 Fire Rate (0-10V) | AO |  |  |  | Range: 0.0 ->100%
Constant Speed Pumps (2)
IN17 | HWP{N}-STS | HW Pump 1 Status | BI |  |  |  | Range: Off/On
IN18 | HWP{N}-STS | HW Pump 2 Status | BI |  |  |  | Range: Off/On
OUT9 | HWP{N}-S/S | HW Pump 1 Start/Stop | BO |  |  |  | Range: Stop/Start
OUT10 | HWP{N}-S/S | HW Pump 2 Start/Stop | BO |  |  |  | Range: Stop/Start
VFD Pumps (2)
IN17 | HWP{N}-STS | HW Pump 1 Status | BI |  |  |  | Range: Off/On
IN18 | HWP{N}-STS | HW Pump 2 Status | BI |  |  |  | Range: Off/On
IN21 | HW-PRESS{N} | HW Differential Pressure 1 | AI | PSI |  |  | Range: 0 ->100% (0-5V)
IN22 | HW-PRESS{N} | HW Differential Pressure 2 | AI | PSI |  |  | Range: 0 ->100% (0-5V)
OUT9 | HWP{N}-S/S | HW Pump 1 Start/Stop | BO |  |  |  | Range: Stop/Start
OUT13 | HWP{N}-SPEED | HW Pump 1 VFD Speed | AO |  |  |  | Range: 0.0 ->100%
OUT10 | HWP{N}-S/S | HW Pump 2 Start/Stop | BO |  |  |  | Range: Stop/Start
OUT14 | HWP{N}-SPEED | HW Pump 2 VFD Speed | AO |  |  |  | Range: 0.0 ->100%
Primary/Secondary Pumps (2P+2S)
IN23 | PRI-HWS-T | Primary Loop HW Supply Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN24 | PRI-HWR-T | Primary Loop HW Return Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN25 | SEC-HWS-T | Secondary Loop HW Supply Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN26 | SEC-HWR-T | Secondary Loop HW Return Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN17 | PHWP{N}-STS | Primary HW Pump 1 Status | BI |  |  |  | Range: Off/On
IN18 | PHWP{N}-STS | Primary HW Pump 2 Status | BI |  |  |  | Range: Off/On
IN19 | SHWP{N}-STS | Secondary HW Pump 1 Status | BI |  |  |  | Range: Off/On
IN20 | SHWP{N}-STS | Secondary HW Pump 2 Status | BI |  |  |  | Range: Off/On
IN13 | PHWP{N}-STS | Primary HW Pump 3 Status | BI |  |  |  | Range: Off/On
IN14 | PHWP{N}-STS | Primary HW Pump 4 Status | BI |  |  |  | Range: Off/On
IN15 | SHWP{N}-STS | Secondary HW Pump 3 Status | BI |  |  |  | Range: Off/On
IN16 | SHWP{N}-STS | Secondary HW Pump 4 Status | BI |  |  |  | Range: Off/On
IN27 | HW-PRESS{N} | HW Differential Pressure | AI | PSI |  |  | Range: 0 ->100% (0-5V)
OUT9 | PHWP{N}-S/S | Primary HW Pump 1 | BO |  |  |  | Range: Stop/Start
OUT10 | PHWP{N}-S/S | Primary HW Pump 2 | BO |  |  |  | Range: Stop/Start
OUT11 | SHWP{N}-S/S | Secondary HW Pump 1 | BO |  |  |  | Range: Stop/Start
OUT13 | SHWP{N}-SPEED | Secondary HW Pump 1 VFD Speed | AO |  |  |  | Range: 0.0 ->100%
OUT12 | SHWP{N}-S/S | Secondary HW Pump 2 | BO |  |  |  | Range: Stop/Start
OUT14 | SHWP{N}-SPEED | Secondary HW Pump 2 VFD Speed | AO |  |  |  | Range: 0.0 ->100%
Mixing Valve
OUT17 | HW-MIXING-VLV | HW Mixing Valve | AO |  |  |  | Range: 0.0 ->100%
Isolation Valves (2)
IN28 | BLR{N}-ISO-VLV-ES | Boiler 1 Isolation Valve End Switch | BI |  |  |  | Range: Close/Open
IN29 | BLR{N}-ISO-VLV-ES | Boiler 2 Isolation Valve End Switch | BI |  |  |  | Range: Close/Open
OUT18 | BLR{N}-ISO-VLV | Boiler 1 Isolation Valve | BO |  |  |  | Range: Close/Open
OUT19 | BLR{N}-ISO-VLV | Boiler 2 Isolation Valve | BO |  |  |  | Range: Close/Open
Combustion Dampers (2)
IN32 | BLR{N}-COMB-DMPR-STS | Boiler 1 Combustion Damper Status | BI |  |  |  | Range: Close/Open
IN33 | BLR{N}-COMB-DMPR-STS | Boiler 2 Combustion Damper Status | BI |  |  |  | Range: Close/Open
Heat Exchanger (single_mod)
IN34 | HX-SUPW-T | Heat Exchanger Supply Water Temp | AI | °F |  |  | Range: 10K -40 ->250
IN35 | HX-RETW-T | Heat Exchanger Return Water Temp | AI | °F |  |  | Range: 10K -40 ->250
OUT22 | HX-VLV | Heat Exchanger Valve (modulating) | AO |  |  |  | Range: 0.0 ->100%
Heat Exchanger (single_onoff)
IN34 | HX-SUPW-T | Heat Exchanger Supply Water Temp | AI | °F |  |  | Range: 10K -40 ->250
IN35 | HX-RETW-T | Heat Exchanger Return Water Temp | AI | °F |  |  | Range: 10K -40 ->250
OUT22 | HX-VLV | Heat Exchanger Valve (on/off) | BO |  |  |  | Range: Close/Open
Heat Exchanger (third_twothird)
IN34 | HX-SUPW-T | Heat Exchanger Supply Water Temp | AI | °F |  |  | Range: 10K -40 ->250
IN35 | HX-RETW-T | Heat Exchanger Return Water Temp | AI | °F |  |  | Range: 10K -40 ->250
OUT22 | HX-VLV-{N}/3 | Heat Exchanger 1/3 Valve | AO |  |  |  | Range: 0.0 ->100%
OUT23 | HX-VLV-{N}/3 | Heat Exchanger 2/3 Valve | AO |  |  |  | Range: 0.0 ->100%
Makeup Water Monitoring
IN36 | MAKEUP-WTR-FLOW | Makeup Water Flow Rate | AI | GPM |  |  | Range: 0 ->100% (0-5V)

## CHW-Plant-Air
SBS Standard I/O Points — CHW-Plant-Air ¦ Updated: 2026-03-31 ¦ Commit: 2cebaa3
Terminal | Point Name | Description | Type | Units | Min | Max | Notes
CHW Plant Core
IN1 | CHWS-T | CHW Supply Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN2 | CHWR-T | CHW Return Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN3 | OAT | Outside Air Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN4 | OAH | Outside Air Humidity | AI | % |  |  | Range: 0 ->100% (0-5V)
IN5 | CHW-FLOW | CHW System Flow | AI | GPM |  |  | Range: 0 ->100% (0-5V)
Chiller Control (2)
IN6 | CHLR{N}-ALARM | Chiller 1 Alarm Contact | BI |  |  |  | Range: Normal/Alarm
IN10 | CHLR{N}-CHWS-T | Chiller 1 Leaving CHW Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN11 | CHLR{N}-CHWR-T | Chiller 1 Entering CHW Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN7 | CHLR{N}-ALARM | Chiller 2 Alarm Contact | BI |  |  |  | Range: Normal/Alarm
IN12 | CHLR{N}-CHWS-T | Chiller 2 Leaving CHW Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN13 | CHLR{N}-CHWR-T | Chiller 2 Entering CHW Temperature | AI | °F |  |  | Range: 10K -40 ->250
OUT1 | CHLR{N}-S/S | Chiller 1 Start/Stop Enable | BO |  |  |  | Range: Stop/Start
OUT2 | CHLR{N}-S/S | Chiller 2 Start/Stop Enable | BO |  |  |  | Range: Stop/Start
Primary CHW Pumps (2)
IN18 | PCHWP{N}-STS | Primary CHW Pump 1 Status | BI |  |  |  | Range: Off/On
IN19 | PCHWP{N}-STS | Primary CHW Pump 2 Status | BI |  |  |  | Range: Off/On
OUT5 | PCHWP{N}-S/S | Primary CHW Pump 1 Start/Stop | BO |  |  |  | Range: Stop/Start
OUT6 | PCHWP{N}-S/S | Primary CHW Pump 2 Start/Stop | BO |  |  |  | Range: Stop/Start
Secondary CHW Pumps (2, 2DP)
IN22 | SCHWP{N}-STS | Secondary CHW Pump 1 Status | BI |  |  |  | Range: Off/On
IN23 | SCHWP{N}-STS | Secondary CHW Pump 2 Status | BI |  |  |  | Range: Off/On
IN26 | CHW-PRESS{N} | CHW Differential Pressure 1 | AI | PSI |  |  | Range: 0 ->100% (0-5V)
IN27 | CHW-PRESS{N} | CHW Differential Pressure 2 | AI | PSI |  |  | Range: 0 ->100% (0-5V)
OUT9 | SCHWP{N}-S/S | Secondary CHW Pump 1 Start/Stop | BO |  |  |  | Range: Stop/Start
OUT13 | SCHWP{N}-SPEED | Secondary CHW Pump 1 VFD Speed | AO |  |  |  | Range: 0.0 ->100%
OUT10 | SCHWP{N}-S/S | Secondary CHW Pump 2 Start/Stop | BO |  |  |  | Range: Stop/Start
OUT14 | SCHWP{N}-SPEED | Secondary CHW Pump 2 VFD Speed | AO |  |  |  | Range: 0.0 ->100%
CHW Bypass Valve
IN38 | CHW-BYP-T | CHW Bypass Temperature | AI | °F |  |  | Range: 10K -40 ->250
OUT30 | CHW-BYP-VLV | CHW Bypass Valve | AO |  |  |  | Range: 0.0 ->100%
Isolation Valves (2)
IN39 | CHLR{N}-CHW-ISO-ES | Chiller 1 CHW Isolation Valve End Switch | BI |  |  |  | Range: Open/Closed
IN40 | CHLR{N}-CHW-ISO-ES | Chiller 2 CHW Isolation Valve End Switch | BI |  |  |  | Range: Open/Closed
OUT31 | CHLR{N}-CHW-ISO | Chiller 1 CHW Isolation Valve | BO |  |  |  | Range: Open/Close
OUT32 | CHLR{N}-CHW-ISO | Chiller 2 CHW Isolation Valve | BO |  |  |  | Range: Open/Close
Makeup Water Monitoring
IN47 | MAKEUP-WTR-FLOW | Makeup Water Flow Rate | AI | GPM |  |  | Range: 0 ->100% (0-5V)

## CHW-Plant-Tower
SBS Standard I/O Points — CHW-Plant-Tower ¦ Updated: 2026-03-31 ¦ Commit: 2cebaa3
Terminal | Point Name | Description | Type | Units | Min | Max | Notes
CHW Plant Core
IN1 | CHWS-T | CHW Supply Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN2 | CHWR-T | CHW Return Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN3 | OAT | Outside Air Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN4 | OAH | Outside Air Humidity | AI | % |  |  | Range: 0 ->100% (0-5V)
IN5 | CHW-FLOW | CHW System Flow | AI | GPM |  |  | Range: 0 ->100% (0-5V)
Chiller Control (2)
IN6 | CHLR{N}-ALARM | Chiller 1 Alarm Contact | BI |  |  |  | Range: Normal/Alarm
IN10 | CHLR{N}-CHWS-T | Chiller 1 Leaving CHW Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN11 | CHLR{N}-CHWR-T | Chiller 1 Entering CHW Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN7 | CHLR{N}-ALARM | Chiller 2 Alarm Contact | BI |  |  |  | Range: Normal/Alarm
IN12 | CHLR{N}-CHWS-T | Chiller 2 Leaving CHW Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN13 | CHLR{N}-CHWR-T | Chiller 2 Entering CHW Temperature | AI | °F |  |  | Range: 10K -40 ->250
OUT1 | CHLR{N}-S/S | Chiller 1 Start/Stop Enable | BO |  |  |  | Range: Stop/Start
OUT2 | CHLR{N}-S/S | Chiller 2 Start/Stop Enable | BO |  |  |  | Range: Stop/Start
Primary CHW Pumps (2)
IN18 | PCHWP{N}-STS | Primary CHW Pump 1 Status | BI |  |  |  | Range: Off/On
IN19 | PCHWP{N}-STS | Primary CHW Pump 2 Status | BI |  |  |  | Range: Off/On
OUT5 | PCHWP{N}-S/S | Primary CHW Pump 1 Start/Stop | BO |  |  |  | Range: Stop/Start
OUT6 | PCHWP{N}-S/S | Primary CHW Pump 2 Start/Stop | BO |  |  |  | Range: Stop/Start
Secondary CHW Pumps (2, 2DP)
IN22 | SCHWP{N}-STS | Secondary CHW Pump 1 Status | BI |  |  |  | Range: Off/On
IN23 | SCHWP{N}-STS | Secondary CHW Pump 2 Status | BI |  |  |  | Range: Off/On
IN26 | CHW-PRESS{N} | CHW Differential Pressure 1 | AI | PSI |  |  | Range: 0 ->100% (0-5V)
IN27 | CHW-PRESS{N} | CHW Differential Pressure 2 | AI | PSI |  |  | Range: 0 ->100% (0-5V)
OUT9 | SCHWP{N}-S/S | Secondary CHW Pump 1 Start/Stop | BO |  |  |  | Range: Stop/Start
OUT13 | SCHWP{N}-SPEED | Secondary CHW Pump 1 VFD Speed | AO |  |  |  | Range: 0.0 ->100%
OUT10 | SCHWP{N}-S/S | Secondary CHW Pump 2 Start/Stop | BO |  |  |  | Range: Stop/Start
OUT14 | SCHWP{N}-SPEED | Secondary CHW Pump 2 VFD Speed | AO |  |  |  | Range: 0.0 ->100%
CW Pumps (2)
IN28 | CDWP{N}-STS | Condenser Water Pump 1 Status | BI |  |  |  | Range: Off/On
IN29 | CDWP{N}-STS | Condenser Water Pump 2 Status | BI |  |  |  | Range: Off/On
OUT17 | CDWP{N}-S/S | Condenser Water Pump 1 Start/Stop | BO |  |  |  | Range: Stop/Start
OUT18 | CDWP{N}-S/S | Condenser Water Pump 2 Start/Stop | BO |  |  |  | Range: Stop/Start
Cooling Towers (2)
IN36 | CDW-ENT-T | Condenser Water Entering Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN37 | CDW-LVG-T | Condenser Water Leaving Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN32 | CT{N}-FAN-STS | Cooling Tower 1 Fan Status | BI |  |  |  | Range: Off/On
IN33 | CT{N}-FAN-STS | Cooling Tower 2 Fan Status | BI |  |  |  | Range: Off/On
OUT21 | CT{N}-FAN-S/S | Cooling Tower 1 Fan Start/Stop | BO |  |  |  | Range: Stop/Start
OUT25 | CT{N}-FAN-SPEED | Cooling Tower 1 Fan VFD Speed | AO |  |  |  | Range: 0.0 ->100%
OUT22 | CT{N}-FAN-S/S | Cooling Tower 2 Fan Start/Stop | BO |  |  |  | Range: Stop/Start
OUT26 | CT{N}-FAN-SPEED | Cooling Tower 2 Fan VFD Speed | AO |  |  |  | Range: 0.0 ->100%
Tower CW Bypass Valve
OUT29 | CT-BYP-VLV | Tower CW Bypass Valve | AO |  |  |  | Range: 0.0 ->100%
Isolation Valves (2+ CDW)
IN39 | CHLR{N}-CHW-ISO-ES | Chiller 1 CHW Isolation Valve End Switch | BI |  |  |  | Range: Open/Closed
IN43 | CHLR{N}-CDW-ISO-ES | Chiller 1 CDW Isolation Valve End Switch | BI |  |  |  | Range: Open/Closed
IN40 | CHLR{N}-CHW-ISO-ES | Chiller 2 CHW Isolation Valve End Switch | BI |  |  |  | Range: Open/Closed
IN44 | CHLR{N}-CDW-ISO-ES | Chiller 2 CDW Isolation Valve End Switch | BI |  |  |  | Range: Open/Closed
OUT31 | CHLR{N}-CHW-ISO | Chiller 1 CHW Isolation Valve | BO |  |  |  | Range: Open/Close
OUT35 | CHLR{N}-CDW-ISO | Chiller 1 CDW Isolation Valve | BO |  |  |  | Range: Open/Close
OUT32 | CHLR{N}-CHW-ISO | Chiller 2 CHW Isolation Valve | BO |  |  |  | Range: Open/Close
OUT36 | CHLR{N}-CDW-ISO | Chiller 2 CDW Isolation Valve | BO |  |  |  | Range: Open/Close
Makeup Water Monitoring
IN47 | MAKEUP-WTR-FLOW | Makeup Water Flow Rate | AI | GPM |  |  | Range: 0 ->100% (0-5V)

## AHU-VAV
SBS Standard I/O Points — AHU-VAV ¦ Updated: 2026-03-31 ¦ IO Schedule Rev
Terminal | Point Name | Description | Type | Units | Min | Max | Notes
AHU Core
IN1 | SF-S | Supply Fan Status | BI |  |  |  | Range: Off/On
IN5 | MAT | Mixed Air Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN6 | SAT | Supply Air Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN7 | RAT | Return Air Temperature | AI | °F |  |  | Range: 10K -40 ->250
IN12 | SA-DSP | Duct Static Pressure | AI | WC |  |  | Range: Table2
OUT1 | OAD | Outside Air Damper | AO |  |  |  | Range: 0.0 ->100%
Supply Fan VFD
OUT9 | SF | Supply Fan Command | BO |  |  |  | Range: Stop/Start
OUT10 | SF-VFD-SPD | Supply Fan VFD Speed | AO |  |  |  | Range: 0.0 ->100%
Return Fan VFD
IN2 | RF-S | Return Fan Status | BI |  |  |  | Range: Off/On
IN14 | BLDG-PRESS | Building Static Pressure | AI | WC |  |  | Range: Table4
OUT11 | RF | Return Fan Command | BO |  |  |  | Range: Stop/Start
OUT12 | RF-VFD-SPD | Return Fan VFD Speed | AO |  |  |  | Range: 0.0 ->100%
Exhaust Fan VFD
IN2 | EF-S | Exhaust Fan Status | BI |  |  |  | Range: Off/On
IN22 | EA-CFM | Exhaust Airflow | AI | CFM |  |  | Range: Table5
IN23 | EA-DMP-ES | Exhaust Damper End Switch | BI |  |  |  | Range: Close/Open
OUT3 | EAD | Exhaust Air Damper | AO |  |  |  | Range: 0.0 ->100%
OUT11 | EF | Exhaust Fan Command | BO |  |  |  | Range: Stop/Start
OUT12 | EF-VFD-SPD | Exhaust Fan VFD Speed | AO |  |  |  | Range: 0.0 ->100%
Relief Fan VFD
IN28 | RLF-S | Relief Fan Status | BI |  |  |  | Range: Off/On
IN14 | BLDG-PRESS | Building Static Pressure | AI | WC |  |  | Range: Table4
OUT14 | RLF | Relief Fan Command | BO |  |  |  | Range: Stop/Start
OUT15 | RLF-VFD-SPD | Relief Fan VFD Speed | AO |  |  |  | Range: 0.0 ->100%
Hot Water Heating
IN8 | HWC-DAT | HW Coil Discharge Air Temp | AI | °F |  |  | Range: 10K -40 ->250
IN31 | HWC-SUPW-T | HW Coil Supply Water Temp | AI | °F |  |  | Range: 10K -40 ->250
IN32 | HWC-RETW-T | HW Coil Return Water Temp | AI | °F |  |  | Range: 10K -40 ->250
OUT4 | HW-VLV | Hot Water Valve (reverse) | AO |  |  |  | Range: 0.0 ->100%
Electric Heat 2-Stage
OUT22 | ELEC-HTR-{N} | Electric Heater Stage 1 | BO |  |  |  | Range: Stop/Start
OUT23 | ELEC-HTR-{N} | Electric Heater Stage 2 | BO |  |  |  | Range: Stop/Start
Gas Heat Modulating
IN44 | GAS-PRSR | Gas Pressure Switch | BI |  |  |  | Range: Normal/Alarm
OUT25 | GAS-VLV | Gas Valve Enable | BO |  |  |  | Range: Stop/Start
OUT29 | GAS-MOD | Gas Modulating Output | AO |  |  |  | Range: 0.0 ->100%
Chilled Water Cooling
IN33 | CHWC-SUPW-T | CHW Coil Supply Water Temp | AI | °F |  |  | Range: 10K -40 ->250
IN34 | CHWC-RETW-T | CHW Coil Return Water Temp | AI | °F |  |  | Range: 10K -40 ->250
OUT5 | CHW-VLV | Chilled Water Valve | AO |  |  |  | Range: 0.0 ->100%
DX Cooling 2-Stage
IN42 | DX-HP | DX High Pressure Switch | BI |  |  |  | Range: Normal/Alarm
IN43 | DX-LP | DX Low Pressure Switch | BI |  |  |  | Range: Normal/Alarm
OUT20 | DX-COMP-{N} | DX Compressor Stage 1 | BO |  |  |  | Range: Stop/Start
OUT21 | DX-COMP-{N} | DX Compressor Stage 2 | BO |  |  |  | Range: Stop/Start
DX Cooling VFD
IN42 | DX-HP | DX High Pressure Switch | BI |  |  |  | Range: Normal/Alarm
IN43 | DX-LP | DX Low Pressure Switch | BI |  |  |  | Range: Normal/Alarm
OUT20 | DX-COMP-{N} | DX Compressor Enable | BO |  |  |  | Range: Stop/Start
OUT27 | DX-VFD-SPD | DX VFD Compressor Speed | AO |  |  |  | Range: 0.0 ->100%
Economizer Dry Bulb
OUT2 | RAD | Return Air Damper (reverse) | AO |  |  |  | Range: 0.0 ->100%
Energy Recovery Wheel
IN11 | ERW-EA-EAT | ERW Exhaust Entering Air Temp | AI | °F |  |  | Range: 10K -40 ->250
IN24 | ERW-STATUS | ERW Status Feedback | BI |  |  |  | Range: Off/On
IN29 | ERW-OA-DAT | ERW OA Leaving Air Temp | AI | °F |  |  | Range: 10K -40 ->250
IN30 | ERW-EA-DAT | ERW Exhaust Leaving Air Temp | AI | °F |  |  | Range: 10K -40 ->250
OUT6 | ERW-OA-BYP-DMP | ERW OA Bypass Damper | AO |  |  |  | Range: 0.0 ->100%
OUT7 | ERW-EA-BYP-DMP | ERW EA Bypass Damper | AO |  |  |  | Range: 0.0 ->100%
OUT13 | ERW | Energy Recovery Wheel Command | BO |  |  |  | Range: Stop/Start
OUT24 | ERW-SPEED | Energy Recovery Wheel VFD Speed | AO |  |  |  | Range: 0.0 ->100%
Preheat Hot Water
IN8 | PH-LAT | Preheat Leaving Air Temp | AI | °F |  |  | Range: 10K -40 ->250
IN35 | PH-EAT | Preheat Entering Air Temp | AI | °F |  |  | Range: 10K -40 ->250
IN39 | PH-SUPW-T | Preheat Coil Supply Water Temp | AI | °F |  |  | Range: 10K -40 ->250
IN40 | PH-RETW-T | Preheat Coil Return Water Temp | AI | °F |  |  | Range: 10K -40 ->250
IN45 | PH-PMP-S | Preheat Pump Status | BI |  |  |  | Range: Off/On
OUT8 | PH-VLV | Preheat Valve (reverse) | AO |  |  |  | Range: 0.0 ->100%
OUT17 | PH-PMP | Preheat Pump Command | BO |  |  |  | Range: Stop/Start
Steam Humidifier
IN10 | RAH | Return Air Humidity | AI | % |  |  | Range: 0 ->100% (0-5V)
IN37 | HUM-STS | Humidifier Status | BI |  |  |  | Range: Off/On
OUT16 | HUM | Humidifier Output | AO |  |  |  | Range: 0.0 ->100%
Dehumidification Subcool
IN10 | RAH | Return Air Humidity | AI | % |  |  | Range: 0 ->100% (0-5V)
IN18 | ZN-RH | Zone Humidity | AI | % |  |  | Range: 0 ->100% (0-5V)
Freeze Protection (LTC)
IN3 | LTC | Low Temperature Cutout | BI |  |  |  | Range: Normal/Alarm
Smoke Detector
IN4 | SMOKE | Duct Smoke Detector | BI |  |  |  | Range: Normal/Alarm
SA High Static Pressure
IN13 | SA-HPS | Supply Air High Static Switch | BI |  |  |  | Range: Normal/Alarm
EA High Static Pressure
IN15 | EA-HPS | Exhaust Air High Static Switch | BI |  |  |  | Range: Normal/Alarm
Filter DP Switch
IN19 | MA-FILT | Mixed Air Filter DP Switch | BI |  |  |  | Range: Clean/Dirty
OA Pre-Filter DP
IN25 | OA-FILT | OA Pre-Filter DP Switch | BI |  |  |  | Range: Clean/Dirty
Final Filter DP
IN26 | FINAL-FILT | Final Filter DP Switch | BI |  |  |  | Range: Clean/Dirty
Exhaust Filter DP
IN27 | EA-FILT | Exhaust Filter DP Switch | BI |  |  |  | Range: Clean/Dirty
Fire Shutdown
IN38 | FIRE-SD | Fire Shutdown Contact | BI |  |  |  | Range: Normal/Alarm
Condensate Overflow
IN36 | COND-OVF | Condensate Overflow Switch | BI |  |  |  | Range: Normal/Alarm
Freeze Stat DP
IN41 | FREEZE-DP | Freeze Stat DP | BI |  |  |  | Range: Normal/Alarm
RA High Static Pressure
IN47 | RA-HPS | Return Air High Static Switch | BI |  |  |  | Range: Normal/Alarm
HW Coil Pump
OUT18 | HW-PMP | HW Coil Pump Command | BO |  |  |  | Range: Stop/Start
CHW Coil Pump
OUT19 | CHW-PMP | CHW Coil Pump Command | BO |  |  |  | Range: Stop/Start